# Buyer Mandate Brief

Normalized mandate for Northstar Models, Inc.

| Opportunity | CB-2026-041 |
| --- | --- |
| Buyer / mandate owner | Northstar Models, Inc. / Maya Chen, Director of Infrastructure Procurement |
| Prepared from | July 29 intake; August 4 workload brief; August 7 procurement follow-up |
| Purpose | Supplier qualification and first-round commercial engagement |

Controlling-source rule: The August 7 procurement follow-up controls where it expressly updates the July 29 intake. The August 4 workload brief controls detailed technical requirements.

# 1. Mandate at a glance

| Field | Controlling position | Class |
| --- | --- | --- |
| Firm capacity | 1,024 NVIDIA B200 SXM GPUs; 128 dedicated eight-GPU HGX B200 nodes | Required |
| Expansion | Option interest for a further 1,024 GPUs; not firm demand | Optional |
| Ramp | 512 GPUs by Jan. 15, 2027; remaining 512 by Feb. 1, 2027 | Required |
| Term | 18 months from first-tranche service; one six-month extension option | Required / option |
| Geography | US East or US Midwest; Virginia preferred | Required / preference |
| Price | $3.10/GPU-hour target; $3.35/GPU-hour hard all-in cap; taxes excluded | Target / cap |
| Prepayment | No more than three months of committed charges | Hard limit |

# 2. Source conflicts resolved

| Topic | Earlier intake | Later instruction | Treatment |
| --- | --- | --- | --- |
| Delivery | All 1,024 by Jan. 1, 2027 | 512 by Jan. 15; 512 by Feb. 1 | Later staged ramp controls |
| Term | 12 months | 18 months plus six-month option | Later term controls |
| Price | $3.10 marked maximum | $3.10 target; $3.35 hard cap | Preserve target and cap |
| Prepayment | Up to four months | Maximum three months | Three-month limit controls |

# 3. Technical requirements

| Area | Requirement |
| --- | --- |
| Deployment | Dedicated homogeneous capacity; no shared or fractional GPU service; no GPU-generation or material node substitution without Northstar's written consent. |
| Workload | Sustained multimodal pretraining, then fine-tuning and evaluation; buyer software image must support its CUDA 13 toolchain. |
| Fabric | At least one 400 Gb/s endpoint per GPU. Dual-rail 800 Gb/s is preferred, not mandatory. |
| External ingress | At least 200 Gb/s committed; 400 Gb/s preferred. |
| Storage | 6 PiB usable shared storage; 1.2 TB/s aggregate sustained read and 800 GB/s aggregate sustained write. |
| Availability | At least 99.5% per calendar month; planned maintenance no more than eight hours per month with at least seven days' notice. |
| Acceptance | 72-hour burn-in, serial and inventory attestation, and NCCL benchmark against a reference and pass threshold agreed before signing. |
| Security | Current SOC 2 Type II; customer-managed encryption keys; United States data residency; exportable administrative and workload-access audit logs; controlled physical access and named-person access records for the GPU hall. |
| Sustainability | Hourly renewable-energy matching is preferred for reporting but is not a condition to proceed. |

# 4. Commercial exposure

Base-term calculation uses the staged ramp and an end boundary of July 15, 2028: 512 GPUs x 17 days x 24 hours, plus 1,024 GPUs x 530 days x 24 hours = 13,234,176 committed GPU-hours.

| Case | Rate | Committed GPU-hours | Estimated base-term charges |
| --- | --- | --- | --- |
| Target | $3.10/GPU-hour | 13,234,176 | $41,025,945.60 |
| Hard cap | $3.35/GPU-hour | 13,234,176 | $44,334,489.60 |

The estimate excludes taxes and the optional expansion. Deposit dollars remain open until the final rate and monthly-hour billing convention are agreed. Any power, implementation, or other pass-through must be tested against the $3.35 all-in cap; egress pricing remains unresolved.

# 5. Open diligence and commercial points

| Priority | Question or evidence | Why it matters |
| --- | --- | --- |
| Signing gate | Confirm the provider legal entity and its control of the offered capacity. | Counterparty authority and performance recourse |
| Signing gate | Provide hardware title, serials, financing liens, and release or consent mechanics. | Avoid unavailable or encumbered inventory |
| Signing gate | Substantiate utility service, facility commissioning, and the two delivery dates. | Delivery credibility |
| Technical | Provide topology, port allocation, carrier order, and benchmark evidence. | Fabric and ingress compliance |
| Acceptance | Agree the NCCL reference configuration and passing threshold. | Objective acceptance |
| Commercial | Confirm egress and non-GPU charges, extension exercise deadline, and extension pricing. | True all-in cost and option value |
| Commercial | Confirm the billing-hour convention and deposit calculation. | Cash exposure |

# 6. Recommended next actions

1 - Supplier evidence: Issue a focused request for entity, capacity-control, title and lien, power, commissioning, network, and security evidence.

2 - Commercial clarification: Require an all-in price build, egress schedule, deposit mechanics, and extension terms before comparing offers.

3 - Technical validation: Review topology, storage architecture, external connectivity, software matrix, and operating history.

4 - Acceptance definition: Freeze the burn-in procedure, inventory attestation, NCCL reference, pass threshold, cure, and retest process in the term sheet.